## Slide 1
Experimental
Survey Data
Evaluate
entropy
ASHRAE
dataset
General base model
Personal
customized
models
Zone
Control
Group
Control
Personal
Control
Result (Comfort, Energy)
Active Transfer Learning
on various amount of surveys
(2)Virtual experimental evaluation
(1)Active Transfer Learning
(Base Dataset)
N=2
Model
Full learning
model
N=20
Model
N=4
Model
(Target Dataset)
Sorted on its entropy
Notes: From last week, I modified the data arrangement part for transfer learning.
I excluded previous comfort agent part and use experimental data directly.
I read previous paper, zenep included user ID using Xgboost algorithm, not for this transfer learning. Since the base model doesn’t include user ID, adding new parameter on transfer learning is not possible.

## Slide 2
(a)Reference building model
(b) Floor plan of target zone
(c)Office area AC Control type
Notes: From last week, I modified the data arrangement part for transfer learning.
I excluded previous comfort agent part and use experimental data directly.
I read previous paper, zenep included user ID using Xgboost algorithm, not for this transfer learning. Since the base model doesn’t include user ID, adding new parameter on transfer learning is not possible.

## Slide 3: Research Target
Integration of Personal Comfort Profiles in Existing HVAC Control Research and OCC Objective Functions Leveraging Differences in Personal Comfort Models
How reducing number of occupant surveys effect comfort and energy usage on different control resolution?
Research Questions
1. Referenceable criteria for data collection on personal comfort survey in actual building control
2. Quantifying the impact of survey reduction on comfort and energy efficiency
Research Contribution
Difficulty of adoption in real building
The number of OCC in real building implementation are still less than simulation studies [3]
While the development of frameworks on simulation is very active, there are still less examples of actual use in real buildings. [4]
Research Background
2. Learning Layer
3. Control Layer
4. HVAC
Layer
1. Sensing Layer
BMS
0. Physical Layer
Occupancy
Comfort
Occupied/
Unoccupied
Counting
Location
Rule Based
MPC
RL
Sensation
Preference
Learning
PID Sensor
RFID
GPS
Wifi
Vision
Occupancy
Learning
Used if
enough
resolution
HVAC(Actuator)
IoT
Voting station
Wearable Device
Feedback via thermostat
Thermal camera
Environment
Voting
[2] Review on occupant centric thermal comfort sensing, predicting, and controlling, Xie et al, 2020
[3] Challenges and opportunities of occupant-centric building controls in real-world implementation: A critical review, Soleimanijavid et al., 2024
Notes: Last month, I shared my current research questions.
And this month, I’ve been working on the second research question, regarding the number of occupant surveys for comfort modeling
I’m intending to submit the conference paper, for Asim in December
____________________________________________
I set research target here
Occupant centric control with less occupant contribution and maximizing occupant acceptance considering individual personal comfort differences
Current research questions are here
First one is regarding How personal comfort profiles are integrated into HVAC control in existing OCC research,
Second one is the effect of reducing number of survey, the effect to comfort and energy usage varied on control resolution

## Slide 4: Research Target for Asim2024 paper
How reducing number of occupant surveys effect control and energy usage on different control resolution?
Research Questions
Personal level control
Purpose of research
To evaluate the impact of the number of comfort surveys on model accuracy and its effect to both energy consumption and occupant comfort.
How this relation would differ depending on HVAC resolution and comfort function setting
2. Learning Layer
3. Control Layer
4. HVAC
Layer
1. Sensing Layer
Result with 2 surveys
65% acceptance
10% Energy saving
Result with 4 surveys
80% acceptance
10% Energy saving
Result with 2 surveys
65% acceptance
5% Energy saving
Result with 4 surveys
65% acceptance
5% Energy saving
Zone level control
Personal
model
…
…
accuracy
60%
accuracy
80%
accuracy
70%
accuracy
85%
accuracy
60%
accuracy
80%
accuracy
70%
accuracy
85%
accuracy
85%
accuracy
80%
Effective
Less Effective?
Two surveys per occupant
Four surveys
Two surveys
Four surveys
Notes: This is the whole image of the experiment, depending on the number of surveys, personal models have variation on its accuracy. Research purpose is to find the effect of amount of survey to model accuracy and building control performance.

## Slide 5: Research Method - Overall framework
1. Developing Personal Thermal Agent Model
2-1. General base model:
General base model is developed using ASHRAE comfort dataset, using CNN-LSTM model.
2-2. Active Transfer Learning:
For developing personal thermal comfort model, the selected instances from (1-2)Virtual Survey answer are used to re-train (2-1)General base model
Various number of survey instances are used to see the effect of to model accuracy
Agent Model
Development
Virtual survey answers
ASHRAE
dataset
General base model
Personal
customized
models
Zone
Control
Group
Control
Personal
Control
Result
(Comfort, Energy)
Active Transfer Learning
on various amount of surveys
(3)MPC control evaluation
3. Virtual experimental Evaluation:
Transfer Learned Models are used in various MPC scenarios
Along the number of training survey instances, its effect to comfort(thermal acceptance) and energy consumption are evaluated.
(2)Active Transfer Learning
(1)Thermal Agent Model
1-1.Thermal Agent Model Creation:
To simulate various occupant’s thermal sensation, agent model are developed using thermal comfort survey data, using multinomial logistic regression based on survey data.
1-2. Generate Virtual Survey Answers:
Virtual survey answers are generated using the created agent models
2. Active Transfer Learning:
Previous
Notes: Here is the framework of this experiment.
1st, I develop personal thermal agent model, based on the survey experimental data. We assume these agents as occupants’ true comfort acceptance expression. And I created virtual survey answers using these agents.
2nd, Active transfer learning was performed to develop various models depending on amounts of survey answers to learn.
Lastly, with these personal customized models, MPC experiment was conducted to see the effect of each models to its performance.

## Slide 6: Research Method - Overall framework
1-1. General base model:
General base model is developed using ASHRAE comfort dataset, using CNN-LSTM model.[8] [9]
1-2. Select survey instances for
Evaluate the existing survey dataset for its informative importance
1-3. Active Transfer Learning:
For developing personal thermal comfort model, the selected instances from experimental dataset are used to re-train (2-1)General base model
Various number of survey instances are used to see the effect of to model accuracy, based on thermal acceptability.
2. Virtual experimental Evaluation:
Transfer Learned Models are used in various rule-based control scenarios
Along the number of training survey instances, its effect to comfort(thermal acceptability) and energy consumption are evaluated.
1. Active Transfer Learning:
[7] Development of the ASHRAE Global Thermal Comfort Database , V. F. Licina, T. Cheung, H. Zhang, R. De Dear, T. Parkinson, E. Arens, C. Chun, S. Schiavon, M. Luo, G. Brager, et al., 2018
[8] A hybrid deep transfer learning strategy for thermal comfort prediction in buildings, Somu et al., 2021
[9] Data-efficient Comfort Modeling: Active Transfer Learning for Predicting Personal Thermal Comfort using Limited Data, Tekler et al., 2024
6
Experimental
Survey Data
Evaluate
entropy
ASHRAE
dataset
General base model
Personal
customized
models
Zone
Control
Group
Control
Personal
Control
Result (Comfort, Energy)
Active Transfer Learning
on various amount of surveys
(2)Virtual experimental evaluation
(1)Active Transfer Learning
(Base Dataset)
N=2
Model
Full learning
model
N=20
Model
N=4
Model
(Target Dataset)
Updated
Sorted on its entropy
Notes: From last week, I modified the data arrangement part for transfer learning.
I excluded previous comfort agent part and use experimental data directly.
I read previous paper, zenep included user ID using Xgboost algorithm, not for this transfer learning. Since the base model doesn’t include user ID, adding new parameter on transfer learning is not possible.

## Slide 7: Method – (1)Active Transfer Learning
Developing base model
General base model was developed using ASHRAE global thermal comfort database[7]
CNN-LSTM model [8] [9] structures was introduced for its high performance in existing research
Active Learning
⇒Select most informative survey instances
Transfer Learning
⇒Leverage existing dataset and knowledge
ASHRAE dataset
Base model
Personalized Re-training
Selected instances
Personal surveys
Fine-tuning
Minimum learning
Model
N=4
Model
Full learning
model
N=20
Model
How much should we add?
Focus on data with high uncertainty
Active Transfer Learning
From the survey instances answered by thermal agent, each survey answer’s the uncertainty for general base model were evaluated
Sorted highest uncertainty survey instances are selected.
Different amount of survey instances are used to re-train ASHRAE base model
Focus on most informative instance
Base
Dataset
Target Dataset
Base model
Target model
Knowledge
N=6
Model
Input : Air temp, RH, Air velocity, Radiate temp
Output : Thermal Acceptability
[7] Development of the ASHRAE Global Thermal Comfort Database , V. F. Licina, T. Cheung, H. Zhang, R. De Dear, T. Parkinson, E. Arens, C. Chun, S. Schiavon, M. Luo, G. Brager, et al., 2018
[8] A hybrid deep transfer learning strategy for thermal comfort prediction in buildings, Somu et al., 2021
[9] Data-efficient Comfort Modeling: Active Transfer Learning for Predicting Personal Thermal Comfort using Limited Data, Tekler et al., 2024
Notes: For the second part, Active transfer learning, I developed the base model first, using AHRAE thermal comfort dataset. CNN-LSTM model structure was used for its high model performance. Input parameters are air temperature, Relative humidity, Air velocity, Radiate temperature, and the output is thermal acceptance.
For transfer learning part, using active learning method, personal surveys are evaluated on the uncertainty for general base model. These survey instances are sorted based on its uncertainty values. Depending on the amount of surveys, these survey instances are picked up and used for re-training. We gain personal thermal models on various number of surveys.

## Slide 8: Result1 – Accuracy of transferred model along the amount of surveys
Chart: Accuracy along the amount of surveys(2)
16 | 0.75 | 0.83333 | 0.91667 | 0.91667 | 0.91667 | 0.91667 | 0.91667 | 0.91667 | 0.91667 | 0.91667
17 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
18 | 0.83333 | 1 | 0.83333 | 0.83333 | 1 | 1 | 1 | 1 | 1 | 1
19 | 0.72727 | 0.72727 | 0.81818 | 0.81818 | 0.81818 | 0.81818 | 0.81818 | 0.81818 | 0.81818 | 0.81818
20 | 0.81818 | 0.81818 | 0.81818 | 0.81818 | 0.72727 | 0.72727 | 0.72727 | 0.72727 | 0.72727 | 0.90909
21 | 0.8 | 0.8 | 0.8 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9
22 | 0.7 | 0.7 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
23 | 0.63636 | 0.63636 | 0.72727 | 0.72727 | 0.72727 | 0.72727 | 0.72727 | 0.72727 | 0.72727 | 0.72727
24 | 0.90909 | 0.72727 | 0.81818 | 0.90909 | 0.90909 | 0.90909 | 0.81818 | 0.90909 | 0.90909 | 0.90909
25 | 0.9 | 0.9 | 1 | 1 | 1 | 1 | 0.9 | 1 | 1 | 0.8
26 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
Chart: Average accuracy along the amount of surveys
| 0 | 2 | 4 | 6 | 8 | 10 | 12 | 14 | 16 | 18 | 20 | ref:full
Average accuracy along the number of surveys | 0.56 | 0.7728 | 0.78044 | 0.82872 | 0.86921 | 0.88092 | 0.88051 | 0.86811 | 0.88092 | 0.88092 | 0.88836 | 0.88
Focus on data with high uncertainty
Occupant
Occupant
Learning Survey Number | 0 | 2 | 4 | 6 | 8 | 10 | 12 | 14 | 16 | 18 | 20 | Ref 100%
Average accuracy along the number of surveys | 56% | 77% | 78% | 83% | 86% | 88% | 88% | 88% | 88% | 88% | 89% | 89%
Ref : Accuracy of full-survey learning
Average of model accuracy was enhanced along the increase of amount of survey, especially at first 5 steps, N =2~8
Chart: Accuracy along the amount of surveys(1)
| 2 | 4 | 6 | 8 | 10 | 12 | 14 | 16 | 18 | 20
1 | 0.81818 | 0.81818 | 0.90909 | 0.90909 | 0.81818 | 0.90909 | 0.81818 | 0.90909 | 0.90909 | 0.90909
2 | 1 | 1 | 0.81818 | 0.72727 | 1 | 1 | 0.90909 | 0.90909 | 0.90909 | 1
4 | 0.90909 | 0.90909 | 0.90909 | 0.90909 | 0.90909 | 0.90909 | 0.90909 | 0.90909 | 0.90909 | 0.90909
5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
6 | 0.72727 | 0.72727 | 0.72727 | 0.81818 | 0.81818 | 0.81818 | 0.81818 | 0.81818 | 0.81818 | 0.81818
7 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6
9 | 0.54545 | 0.54545 | 0.81818 | 0.81818 | 0.81818 | 0.81818 | 0.81818 | 0.81818 | 0.81818 | 0.90909
10 | 0.90909 | 0.90909 | 0.90909 | 0.90909 | 0.90909 | 0.90909 | 0.90909 | 0.90909 | 0.90909 | 0.90909
12 | 0.81818 | 0.81818 | 0.90909 | 0.90909 | 0.90909 | 0.90909 | 0.90909 | 0.90909 | 0.90909 | 0.90909
13 | 0.6 | 0.7 | 0.7 | 1 | 1 | 1 | 1 | 1 | 1 | 1
14 | 0.5 | 0.5 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
Notes: Here is the updated average accuracy of transfer learning with different amount of survet
Here is the 1st result of active transfer learning, I’m showing the relation of average accuracy and the amount of survey on left upper graph and \each occupant’s relation on the right side graph.
total survey dimension are about one hundred. So we can see the first model with 2% amount of surveys reach 64% accuracy and this accuracy improves as the number of survey increase. Around 30% of adding instances, these model’s average accuracy reached 89%.
As a reference, the model that used all the survey instances reaches 88%.

## Slide 9: Method – (3) OCC control evaluation
Addressing discrepancies of PMV with individual thermal comfort
In HVAC control, setpoint control considering PMV is orthodox method.
However, it has been reported that PMV control, which assumes an average comfort level, can result in only about 34% of people being satisfied due to discrepancies with individual thermal comfort. [1]
Difference between PMV and actual acceptance
Difference of thermal comfort
MPC Control Type
Survey amount for learning
N=2
N=4
Full survey
…
…
Group
Control
(VAV+4Fans)
Zone
Control
(VAV)
Personal
Control
(VAV+16Fans)
Difference of energy consumption
Notes: Using these models, I tried to integrate them into MPC setting to see the effect to thermal comfort and energy consumption

## Slide 10
Virtual experiment setting
Using various models on different number of surveys, its effect to HVAC control performance was evaluated.
For virtual experiment, energy plus model of large office building in Singapore was used[9].
Target building is conditioned with VAV, equipped with ceiling fans, according to its control methods
3 rule-based control types (Zone, Group, Personal control) are assumed to set temperature setpoint
Calculation was conducted for one-month period in October
Occupancy schedule was created utilizing occupancy simulator [10]
Duarte, C., Raftery, P., Schiavon, S., 2018. Development of whole-building energy models for detailed energy insights of a large office building with green certification rating in Singapore.
[9] Development of Whole‐Building Energy Models for Detailed Energy Insights of a Large Office Building with Green Certification Rating in Singapore, Duarte, C., Raftery, P., Schiavon, S., 2018
[10] An agent-based stochastic Occupancy Simulator, Chen et al, 2018
(a)Reference building model
(b) Floor plan of target zone
Office area AC Control type
Method – (3) OCC control evaluation
Notes: I used energy plus model of large office building in Singapore, which was conditioned basically VAV and equipped with ceiling fans.
Three control types are assumed, VAV system for zone control and Hybrid system for group and personal control.

## Slide 11: Method – (3) Rule-based control
Difference between PMV and actual acceptance
Control type | AC System | Num of occupant per control area | To satisfy…
Zone | VAV | 16 | To find temp setpoint which maximize occupant acceptability
Group | Hybrid (VAV+ 4 Ceiling Fan) | 4 | To find temp setpoint which maximize occupant acceptability it with group fan mode
Personal | Hybrid (VAV+ 16Ceiling Fan) | 1 | To find temp setpoint which maximize occupant acceptability it with personal fan mode
Control rule
Notes: I set the control like written here. For zone control, maximum temperature setpoint would be selected to make 75% of occupant satisfy.
For group and personal controls, temperature setpoint would be selected to satisfy 75% of occupant with proper fan modes.
I already deploy zone control and personal control, but group personal control part is still undergoing.

## Slide 12: Method – Evaluation
Evaluation method
Developing Personal Thermal Model
Control performance, controlled by transferred model would be evaluated with full-learned model as a reference
Various models developed by different amount of survey would be evaluated.
Experimental
Survey Data
Evaluate
uncertainty
ASHRAE
dataset
General base model
Personal
customized
models
Zone
Control
Group
Control
Personal
Control
Result (Comfort, Energy)
Active Transfer Learning
on various amount of surveys
(2)Virtual experimental evaluation
(1)Active Transfer Learning
(Base Dataset)
N=2
Model
Full learning
model
N=20
Model
N=4
Model
(Target Dataset)
Reference
How mush selected control setpoints are actually comfortable?
Notes: I modified this part, how to evaluate the model performance.
I decided to use the full learning model as reference, and tried to see how the control performance converged.
The result of control would be evaluated in terms of energy and comfort. For comfort evaluation, the thermal agent model’s survey answers are used as a true comfort acceptance.

## Slide 13: Result2 – The effect of amount of learning instances to thermal acceptance
Difference between PMV and actual acceptance
Zone Control
Personal Control
Mean thermal acceptability on selected environment was improved more quickly, for both zone control and personal control.
Thermal acceptability of personal control get stable more quickly than zone control, because occupant has wider choice of their suggested environment
Chart: Comfort performance improvement, compared with full-learning model
| base | 2 | 4 | 6 | 8 | 10 | 12 | 14 | 16 | 18 | 20 | ref: full
mean_acceptability_ratio | 0.76964 | 0.95522 | 0.96928 | 0.93511 | 0.9645 | 0.94981 | 0.93922 | 0.99743 | 0.93929 | 0.93372 | 0.94637 | 1
Under review
Chart: Average accuracy along the amount of surveys
| 0 | 2 | 4 | 6 | 8 | 10 | 12 | 14 | 16 | 18 | 20 | ref:full
Average accuracy along the number of surveys | 0.56 | 0.7728 | 0.78044 | 0.82872 | 0.86921 | 0.88092 | 0.88051 | 0.86811 | 0.88092 | 0.88092 | 0.88836 | 0.88
Ref : Accuracy of full-survey learning
Chart: Comfort performance improvement, compared with full-learning model
| base | 2 | 4 | 6 | 8 | 10 | 12 | 14 | 16 | 18 | 20 | ref: full
 | 0.36585 | 0.49526 | 0.72015 | 0.85208 | 0.97269 | 0.9595 | 0.9661 | 0.94631 | 0.91589 | 0.98061 | 0.98061 | 1
Under review
Notes: Here is the result of comfort performance based on thermal acceptability,
But there seems some errors so I’m reviewing on the code again
Here is the result of thermal acceptability on zone control and personal control. As we set the rule to select temperature to satisfy 75% of occupant, 75% is a basic goal line.
While the model’s accuracy improves in linear, the MPC performance improves quickly, compared to accuracy.
For the case of zone control, the control performance increase quickly at first three models, and reach the target of 75% satisfaction with 12% of data amount.
For the case of personal control, the MPC performance are not stable but after around 16% of survey amount, the control performance get stable.

## Slide 14: Current Conclusion
Addressing discrepancies of PMV with individual thermal comfort
In HVAC control, setpoint control considering PMV is orthodox method.
However, it has been reported that PMV control, which assumes an average comfort level, can result in only about 34% of people being satisfied due to discrepancies with individual thermal comfort. [1]
Difference between PMV and actual acceptance
☑ Calculation on group comfort
☑ Try to enhance the model’s accuracy
Next Step before ASim paper submission (Sep 5th)
☑ Calculation on group comfort
☑ Try to enhance the model’s accuracy
☑ The effect of amount of survey instance for learning, to its accuracy and virtual OCC performance was evaluated.
☑ Accuracy improves along the amount of learning surveys, especially at N=2~8
☑ Surveys with only two instances significantly improve the accuracy, which is enough for AC control strategy.
Notes: Here is the current result
The effect of amount of learning survey instances, to its accuracy and MPC performance were evaluated.
Accuracy was improved along the amount of survey instances
We can see 10 to 15% amount of comfort survey, from control environmental range works well to control HVAC system properly.
As a next step, I should develop group comfort model and enhance the model accuracy more.

## Slide 15: - Active learning with XG-Boost algorithm (one choice of random tree) would include several models in one models, as a brunch of personal model - Active transfer learning using Deep Learning would not include personal ID, since base model won’t include personal detection ID Since gaining complete thermal comfort profiles for various occupant is not feasible, Usual step learning(if not know which environment is informative? ) Active learning(if which environment is informative?) 100% learning(If all the profiles were known? )

## Slide 16: EOF

## Slide 17: Ref:A hybrid deep transfer learning strategy for thermal comfort prediction in buildings,
Novel example to leverage existing dataset and to capture the spatio and temporal information
①The significant Thermal Comfort Parameters(TCPs) contributing the model performance
②The significance of the spatial and temporal information
③The effect of the size of the target dataset
Proposed TL CNN-LSTM framework
Comfort modeling knowledge is transferred from source domain (ASHRAE dataset) to target domain (Medium US office dataset)
Initial CNN layer (9*1), two LSTM layer will take spatio and temporal information from thermal comfort parameters
Proposed model outperforms Random forest and CNN-LSTM
Shown that 15% of training dataset, the accuracy of TL CNN-LSTM significantly improved
Minimum amount of survey data could be explained not in percentage of training dataset
Transfer learning
with source dataset (ASHRAE) and target dataset (US office)
Improving accuracy
along the survey amount
Background
&
Project target
Methodology
Success
Limitation
Concept of transfer learning
Notes: our team developped framework to reduce the number of occupant survey using deep learning method like transfer learing and active learningwith transfer learning we can leverage the knowledge of other large data source into our personal model.

## Slide 18: Ref: Data-efficient Comfort Modeling: Active Transfer Learning for Predicting Personal Thermal Comfort using Limited Data
Proposed ATL-CNNLSTM models, integrating both transfer learning and active learning
Transfer Learning : Retrained by target domain BCA dataset, after trained by ASHRAE source domain dataset
Active Transfer Learning : Select the most informative survey samples by Query-By-Committee learning
Reduced comfort survey by integrating transfer and active learning
Background
&
Project target
Aim to reduce required amounts of comfort survey and identify minimum number
Methodology
Success
Achieve higher accuracy than usual CNNLSTM method
Learning with just two samples achieve almost same accuracy with full-samples learning, higher accuracy than normal CNNLSTM
Limitation
Can be explored how to get the most informative survey in actual building operation
Accuracy evaluation is aggregated, so there can be a variation of accuracy between occupants
Active Learning
⇒Select most informative survey instances
Transfer Learning
⇒Leverage existing
dataset and knowledge
Existing dataset
Foundation model
Personal Customized Model
Selected instances
Personal surveys
Fine-tuning
Combination and transfer learning and active learning
High prediction accuracy
with only two instances
Notes: additionally using active learning we canfocus on the most informative environmental condition regarding the thermal comfort.now we can achieve high prediction accuracy for thermal comfort only with two surveys.

## Slide 19: Experiment for Asim paper
Exploring the Impact of Survey Resolution on the Accuracy of Personal Thermal Comfort Models Using Transfer Learning
Title
ASHRAE Thermal
comfort database
Research flow
Tropic countries
Survey
3500 surveys
- Indonesia
- Singapore
- Philippines
- Malaysia
- Thailand
Purpose
Investigate the relationship of number of thermal comfort survey and its prediction accuracy
Research Flow
1. (☑ done) Develop general thermal comfort model, based on ASHRAE thermal comfort survey, filtered for only tropics country
2. (☑ done) Develop personal comfort model by transfer learning, using BCA experiment survey ← Might replace for better data
3. (☑ done) See the difference of prediction accuracy, varied on the number or survey for re-training
4. (not yet ) Run the RL control with different accuracy comfort model and see the effect of comfort and energy
General
Thermal
Comfort
Model
Input
(Air temp, RH,
Air velocity)
Output
(Thermal
sensation)
BCA survey
On Stable thermal state
Personal
Comfort
Models
(Might be replaced
to other dataset)
29 subject occupant
35 surveys for each
1. Develop general thermal comfort model
2. Develop personal comfort model using transfer learning
Comfort model
Test_1
Comfort model
Test_2
Comfort model
Test_3
Comfort model
Test_n
…
3. Compare accuracies,
varied by re-learning data
amount
Transfer
Learning
Accuracy
Test_1
Accuracy
Test_2
Accuracy
Test_3
Accuracy
Test_n
4. Run control with varied comfort models
To be designed
In detail
Not necessary for this conference?
Input
(Air temp, RH,
Air velocity)
Output
(Thermal
sensation)
Research Object
- Investigate the relationship of number of thermal comfort survey and its prediction accuracy
(See the difference of energy and comfort reward on RL control building, varied on model’s prediction accuracy)
Notes: I started experiment related to second research question.
I created the general thermal comfort model by ASHRAE comfort database in tropics countries, and update personal comfort models using BCA survey data.
It’s still practice but I think I can replace this data
I’m trying to see the difference of accuracy, based on number of learning data

## Slide 20: Result2 – The effect of amount of learning instances to energy consumption
Difference between PMV and actual acceptance
Chart: Energy Consumption along the ratio of survey instances
| 1.9607843137254902E-2 | 3.9215686274509803E-2 | 5.8823529411764705E-2 | 7.8431372549019607E-2 | 9.8039215686274508E-2 | 0.11764705882352941 | 0.13725490196078433 | 0.15686274509803921 | 0.17647058823529413 | 0.19607843137254902 | 0.21568627450980393 | 0.23529411764705882 | 0.25490196078431371 | 0.27450980392156865 | 0.29411764705882354
Eall_sum | 491.3158 | 550.948 | 576.1069 | 575.472 | 567.9034 | 584.3183 | 592.9604 | 593.0801 | 591.49 | 590.3633 | 590.2141 | 589.871 | 582.1891 | 582.4823
Chart: Energy Consumption along the ratio of survey instances
| 1.9607843137254902E-2 | 3.9215686274509803E-2 | 5.8823529411764705E-2 | 7.8431372549019607E-2 | 9.8039215686274508E-2 | 0.11764705882352941 | 0.13725490196078433 | 0.15686274509803921 | 0.17647058823529413 | 0.19607843137254902 | 0.21568627450980393 | 0.23529411764705882 | 0.25490196078431371 | 0.27450980392156865 | 0.29411764705882354
mean_acceptance_avg | 424.3148 | 423.7697 | 449.8163 | 460.9741 | 443.574 | 475.1261 | 457.6754 | 468.5955 | 474.9347 | 470.1441 | 480.0837 | 476.8698 | 474.5654 | 472.6435
Zone Control
Personal Control
With model learned by less amount of surveys, MPC algorithm tend to choose higher setpoint, for its less acceptance prediction accuracy.
As the model’s accuracy improve, the MPC algorithm choose proper temperature setpoint, that contribute to increase of energy consumption.
Chart: Average model accuracy along the amount of surveys
| 1.9607843137254902E-2 | 3.9215686274509803E-2 | 5.8823529411764705E-2 | 7.8431372549019607E-2 | 9.8039215686274508E-2 | 0.11764705882352941 | 0.13725490196078433 | 0.15686274509803921 | 0.17647058823529413 | 0.19607843137254902 | 0.21568627450980393 | 0.23529411764705882 | 0.25490196078431371 | 0.27450980392156865 | 0.29411764705882354
Average accuracy along the number of surveys | 0.64426 | 0.68347 | 0.69748 | 0.69748 | 0.68908 | 0.71148 | 0.73109 | 0.7479 | 0.73109 | 0.77311 | 0.7535 | 0.80672 | 0.84034 | 0.86835 | 0.88515
Ref : Accuracy of full-survey learning
Notes: This is the result of energy consumption for zone control and personal control.
At early phase, MPC control method would try to set temperature setpoint higher as much as possible.
Along the improvement of personal model accuracy, proper temperature setpoint would be selected, considering occupant schedule and acceptance.

## Slide 21: Result1 – Accuracy of transferred model along the amount of surveys
Focus on data with high uncertainty
Chart: Accuracy along the amount of surveys(1)
| 1.9607843137254902E-2 | 3.9215686274509803E-2 | 5.8823529411764705E-2 | 7.8431372549019607E-2 | 9.8039215686274508E-2 | 0.11764705882352941 | 0.13725490196078433 | 0.15686274509803921 | 0.17647058823529413 | 0.19607843137254902 | 0.21568627450980393 | 0.23529411764705882 | 0.25490196078431371 | 0.27450980392156865 | 0.29411764705882354
2 | 0.52381 | 0.52381 | 0.61905 | 0.61905 | 0.47619 | 0.66667 | 0.66667 | 0.71429 | 0.66667 | 0.61905 | 0.71429 | 0.85714 | 0.95238 | 0.95238 | 1
3 | 0.66667 | 0.61905 | 0.61905 | 0.66667 | 0.80952 | 0.66667 | 0.71429 | 0.71429 | 0.66667 | 0.61905 | 0.71429 | 0.61905 | 0.85714 | 0.7619 | 0.90476
5 | 0.61905 | 0.66667 | 0.61905 | 0.61905 | 0.66667 | 0.66667 | 0.66667 | 0.85714 | 0.66667 | 0.80952 | 0.80952 | 0.90476 | 0.80952 | 0.80952 | 0.80952
6 | 0.66667 | 0.7619 | 0.80952 | 0.80952 | 0.80952 | 0.71429 | 0.80952 | 0.80952 | 0.71429 | 0.71429 | 0.80952 | 0.80952 | 0.80952 | 0.85714 | 0.80952
7 | 0.71429 | 0.7619 | 0.7619 | 0.7619 | 0.7619 | 0.7619 | 0.90476 | 0.90476 | 0.90476 | 0.95238 | 0.7619 | 0.95238 | 0.95238 | 0.95238 | 0.95238
9 | 0.61905 | 0.71429 | 0.85714 | 0.71429 | 0.61905 | 0.7619 | 0.66667 | 0.71429 | 0.7619 | 0.80952 | 0.71429 | 0.71429 | 0.7619 | 0.85714 | 0.90476
12 | 0.47619 | 0.47619 | 0.52381 | 0.57143 | 0.66667 | 0.52381 | 0.52381 | 0.61905 | 0.71429 | 0.61905 | 0.66667 | 0.66667 | 0.61905 | 0.71429 | 0.7619
14 | 0.80952 | 0.90476 | 0.80952 | 0.80952 | 0.85714 | 0.80952 | 0.80952 | 0.80952 | 0.80952 | 0.80952 | 0.7619 | 0.85714 | 0.95238 | 1 | 0.85714
16 | 0.52381 | 0.57143 | 0.38095 | 0.42857 | 0.47619 | 0.61905 | 0.66667 | 0.66667 | 0.57143 | 0.90476 | 0.66667 | 0.66667 | 0.7619 | 0.66667 | 0.80952
Chart: Accuracy along the amount of surveys(2)
| 1.9607843137254902E-2 | 3.9215686274509803E-2 | 5.8823529411764705E-2 | 7.8431372549019607E-2 | 9.8039215686274508E-2 | 0.11764705882352941 | 0.13725490196078433 | 0.15686274509803921 | 0.17647058823529413 | 0.19607843137254902 | 0.21568627450980393 | 0.23529411764705882 | 0.25490196078431371 | 0.27450980392156865 | 0.29411764705882354
17 | 0.57143 | 0.61905 | 0.61905 | 0.57143 | 0.52381 | 0.57143 | 0.61905 | 0.61905 | 0.61905 | 0.80952 | 0.57143 | 0.85714 | 0.85714 | 0.85714 | 0.90476
18 | 0.7619 | 0.71429 | 0.7619 | 0.7619 | 0.7619 | 0.7619 | 0.7619 | 0.7619 | 0.7619 | 0.7619 | 0.80952 | 0.80952 | 0.80952 | 0.80952 | 0.80952
19 | 0.42857 | 0.7619 | 0.85714 | 0.95238 | 0.85714 | 0.85714 | 0.80952 | 0.80952 | 0.7619 | 0.80952 | 0.85714 | 0.95238 | 0.95238 | 1 | 1
20 | 0.61905 | 0.52381 | 0.52381 | 0.66667 | 0.80952 | 0.7619 | 0.80952 | 0.85714 | 1 | 1 | 0.85714 | 0.90476 | 0.90476 | 0.95238 | 0.90476
23 | 0.80952 | 0.85714 | 0.7619 | 0.7619 | 0.7619 | 0.71429 | 0.7619 | 0.71429 | 0.61905 | 0.71429 | 0.71429 | 0.71429 | 0.80952 | 0.90476 | 0.95238
24 | 0.66667 | 0.66667 | 0.85714 | 0.61905 | 0.47619 | 0.7619 | 0.80952 | 0.61905 | 0.66667 | 0.66667 | 0.7619 | 0.7619 | 0.7619 | 0.85714 | 0.85714
25 | 0.7619 | 0.7619 | 0.80952 | 0.80952 | 0.71429 | 0.7619 | 0.7619 | 0.71429 | 0.7619 | 0.7619 | 0.7619 | 0.7619 | 0.7619 | 0.85714 | 0.85714
26 | 0.71429 | 0.71429 | 0.66667 | 0.71429 | 0.66667 | 0.71429 | 0.66667 | 0.80952 | 0.7619 | 0.7619 | 0.85714 | 0.90476 | 0.95238 | 0.95238 | 0.95238
Occupant
Chart: Average accuracy along the amount of surveys
| 1.9607843137254902E-2 | 3.9215686274509803E-2 | 5.8823529411764705E-2 | 7.8431372549019607E-2 | 9.8039215686274508E-2 | 0.11764705882352941 | 0.13725490196078433 | 0.15686274509803921 | 0.17647058823529413 | 0.19607843137254902 | 0.21568627450980393 | 0.23529411764705882 | 0.25490196078431371 | 0.27450980392156865 | 0.29411764705882354
Average accuracy along the number of surveys | 0.64426 | 0.68347 | 0.69748 | 0.69748 | 0.68908 | 0.71148 | 0.73109 | 0.7479 | 0.73109 | 0.77311 | 0.7535 | 0.80672 | 0.84034 | 0.86835 | 0.88515
Occupant
 | 2.0% | 3.9% | 5.9% | 7.8% | 9.8% | 11.8% | 13.7% | 15.7% | 17.6% | 19.6% | 21.6% | 23.5% | 25.5% | 27.5% | 29.4% | Ref 100%
Average accuracy along the number of surveys | 64% | 68% | 70% | 70% | 69% | 71% | 73% | 75% | 73% | 77% | 75% | 81% | 84% | 87% | 89% | 88%
Ref : Accuracy of full-survey learning
Average of model accuracy was enhanced along the increase of amount of survey.
With 30% of learning data, the accuracy reached to one of the model, learned by full survey instances.
-> Trying to find the modeling setting, to reach higher accuracy in early amount stage
Notes: Here is the 1st result of active transfer learning, I’m showing the relation of average accuracy and the amount of survey on left upper graph and \each occupant’s relation on the right side graph.
total survey dimension are about one hundred. So we can see the first model with 2% amount of surveys reach 64% accuracy and this accuracy improves as the number of survey increase. Around 30% of adding instances, these model’s average accuracy reached 89%.
As a reference, the model that used all the survey instances reaches 88%.
Actually, the accuracy was not as high as I expected, so I’m trying to develop the model with higher accuracy in early stage.

## Slide 22: Method – (1)Thermal Agent Model
Thermal agent model, showing true comfort
Thermal comfort dataset collected by the experiment[4] was used to develop thermal comfort agent models
Multinomial logistic regression was used to create the possibility curve of for each agent [5] [6], expressed as relation with SET*
With the developed thermal agent model, possibility of thermal acceptance to each environmental condition was calculated
Then, possibility was converted to 1(accept) 0(not accept) with threshold of 0.5
Generate Virtual Survey Answers
Thermal Agent models
Indoor Temp
(22~30 °C( Δ 0.5 °C) )
×
Ceiling Fan mode
5 fan modes
Temp | Fan Mode | Object 1 | Object 2
22 | 0 | ○ | ○
22 | … | … | …
22 | 5 | × | ○
22.5 | 0 | ○ | ○
… | … | … | …
30 | 5 | × | ○
Possibility of
no-change preference
Existing
survey dataset
[4] Effects of temperature, air movement and initial metabolic rate on thermal sensation during transient state in the tropics., Mihara et al, 2019, Building and Environment
[5] The Impact of Resolution of Occupancy Data on Personal Comfort Model-Based HVAC Control Performance, Ono et al., 2022, BuildSym22
[6] Energy saving potentials of integrating personal thermal comfort models for control of building systems: Comprehensive quantification through combinatorial consideration of influential parameters, Jimg and Jazizadeh, 2020, Applied Energy
18 subject
24-30 °C Indoor Temp
5 fan modes
102 environmental conditions
5% of noise values were added to introduce randomness
Notes: I developed thermal agent model that express thermal acceptance in relation with SET*, from the experiment survey data Mihara-san conducted before.
We can calculate the possibility of thermal acceptance on each occupant.
With this possibility curve, I generate the virtual survey answers using the possibility of thermal acceptance, and then convert it to accepted and not accepted with threshold of 0.5

## Slide 23: Research Target for Asim2024 paper
The effect of reducing number of occupant surveys to comfort modeling’s accuracy and its effect comfort and energy usage on different control resolution
Research Objective
Advantage
of OCC
Effort for
OCC
- To evaluate the impact of the number of comfort surveys on model accuracy and its effect to both energy consumption and occupant comfort.
- The investigation is based on data-efficient comfort modeling using the Active Transfer Learning (ACTL-CNNLSTM) model.
Purpose of research
Relation between prediction accuracy and learning data amount
[2] Review on occupant centric thermal comfort sensing, predicting, and controlling, Xie et al, 2020
[3] Challenges and opportunities of occupant-centric building controls in real-world implementation: A critical review, Soleimanijavid et al., 2024

## Slide 24: Research for Asim
Research Purpose
Needs to be updated
Comfort Agent Model Creation:
A Comfort Agent Model is developed using Multinomial Logistic Regression based on survey data. This model predicts individual occupant comfort levels in various thermal environments.
Generate Virtual Survey Answers:
Virtual survey answers are generated using the Comfort Agent Model, simulating agent responses to different thermal conditions. A 5% random variation is added to these answers to mimic real-world variability.
Transfer Learning:
The generated Virtual Survey Answers are used to fine-tune a General Model, pre-trained on the ASHRAE dataset, through transfer learning. This process adapts the General Model to the specific comfort preferences of each agent, resulting in a Transfer Learned Model for each agent.
Model Predictive Control (MPC) Evaluation:
The Transfer Learned Models are used in various Model Predictive Control scenarios to manage environmental conditions. The effectiveness of these MPC strategies is then compared against the original Comfort Agent Model to evaluate the improvements achieved through transfer learning.
Notes: I set research target here
Occupant centric control with less occupant contribution and maximizing occupant acceptance considering individual personal comfort differences
Current research questions are here
First one is regarding How personal comfort profiles are integrated into HVAC control in existing OCC research,
Second one is the effect of reducing number of survey, the effect to comfort and energy usage varied on control resolution

## Slide 25: Research Target for Asim2024 paper
The effect of reducing number of occupant surveys to comfort modeling’s accuracy and its effect comfort and energy usage on different control resolution
Research Objective
Advantage
of OCC
Effort for
OCC
- To evaluate the impact of the number of comfort surveys on model accuracy and its effect to both energy consumption and occupant comfort.
- The investigation is based on data-efficient comfort modeling using the Active Transfer Learning (ACTL-CNNLSTM) model.
Purpose of research
Relation between prediction accuracy and learning data amount
[2] Review on occupant centric thermal comfort sensing, predicting, and controlling, Xie et al, 2020
[3] Challenges and opportunities of occupant-centric building controls in real-world implementation: A critical review, Soleimanijavid et al., 2024

## Slide 26: Background of research
[1] Analysis of the accuracy on PMV – PPD model using the ASHRAE Global Thermal Comfort Database II
[2]Review on occupant centric thermal comfort sensing, predicting, and controlling, Xie et al, 2020
[3] Challenges and opportunities of occupant-centric building controls in real-world implementation: A critical review, Soleimanijavid et al., 2024
[4] A critical review of field implementations of occupant-centric building controls, Park et al., 2019
Addressing discrepancies of PMV with individual thermal comfort
In HVAC control, setpoint control considering PMV is orthodox method.
However, it has been reported that PMV control, which assumes an average comfort level, can result in only about 34% of people being satisfied due to discrepancies with individual thermal comfort. [1]
Difference between PMV and actual acceptance
In building air conditioning industry, Occupant-Centric Control (OCC), has been gaining attentions these years to integrate human element into building control [2]
OCC aims to optimize air-conditioning system (such as temperature setpoint, ceiling fan mode) automatically to pursue ①Occupant comfort ②Energy saving
Introduction – Purpose of OCC
Difficulty of adoption in real building
The number of OCC in real building implementation are still less than simulation studies [3]
While the development of frameworks on simulation is very active, there are still less examples of actual use in real buildings. [4]
2. Learning Layer
3. Control Layer
4. HVAC
Layer
1. Sensing Layer
BMS
0. Physical Layer
Occupancy
Comfort
Occupied/
Unoccupied
Counting
Location
Rule Based
MPC
RL
Sensation
Preference
Learning
PID Sensor
RFID
GPS
Wifi
Vision
Occupancy
Learning
Used if
enough
resolution
HVAC(Actuator)
IoT
Voting station
Wearable Device
Feedback via thermostat
Thermal camera
Environment
Voting
Notes: in building air conditioning industry, occupant centric control, OCC is gathering attention these years. OCC integrates human perception for the environmental condition, such as feeling cold, cool, neutral, warm, hot the purpose of occ is maximize occupant comfort while minimizing energy consumption
for developing occ, three basic components would be integrated. namely sensing layor for measuring environment or occupant occupancy and preference. developing prediction model to infer like how this person would feel under specic environment. the last part is control layer, deciding how to control temperature or fan speed considering these model

## Slide 27: Difficulty of application of OCC
Relation between prediction accuracy and learning data amount
2. Learning Layer
3. Control Layer
4. HVAC
Layer
1. Sensing Layer
BMS
0. Physical Layer
Occupancy
Comfort
Occupied/
Unoccupied
Counting
Location
Rule Based
MPC
RL
Sensation
Preference
Learning
PID Sensor
RFID
GPS
Wifi
Vision
Occupancy
Learning
Used if
enough
resolution
HVAC(Actuator)
IoT
Voting station
Wearable Device
Feedback via thermostat
Thermal camera
Environment
Voting
[2] Review on occupant centric thermal comfort sensing, predicting, and controlling, Xie et al, 2020
[3] Challenges and opportunities of occupant-centric building controls in real-world implementation: A critical review, Soleimanijavid et al., 2024
Notes: one of the issue for applying occ into real building operation is the difficulty of creating personal comfort model for each occupants. it requires gaining dozenscomfort survey from each ocupant